## Slide 1: Gersemi Cryostat
Control System and Automatic Sequences
ACS – J.P. Thermeau
3rd Follow-up meeting – 15th February 2017

## Slide 2: General questions/comments to ACS
4. Please add a state diagram that shows all allowed sequence combinations and conditions for transitions between them.
What do you want exactly ?
5. It is desirable that the PLC program, when doing the check before starting the sequence, takes into account only the actuators/sensors that are used in a given sequence and all other active sequences for the actual insert. For this we need such a list for every sequence and insert.
The list of the actuators/sensors exists for each sequence. I will do this list for the inserts.
6. In many sequences the first state (STOP-state 0 – sequence not active) contains some actions. It looks like it is more a description of an expected situation before starting given sequence or a condition to start a sequence rather than an action that should be executed whenever this sequence is not running. If the text in the action box of state 0 is a condition to start the sequence it should be moved to the proper place (see attachments “Sequence 1” and “Sequence 9” as examples).
I agree, I modified the sequences.

## Slide 3: General questions/comments to ACS
7. Before every sequence it should be clearly written for what insert it is done.
I will add a comment.
8. Please define the state of the ”switch valves” for “normal operation”. There are many different “normal operations” so we need to program the state of the valve for each mode. There probably should be a sequence(s) running all the time that sets up and maintains the different modes (different inserts, gas bag/compressor). See “Switch valve modes” at the end of this document.
What do you want exactly ? The user chooses the position of the switch valves.
9. Relates to point 4. All sequences should have written what sequences are allowed to run in parallel and which must be forbidden.
In the manual mode, I suppose that the user is competent to use this equipment, but it is possible to limit the choice of the user, I will define a normal path.

## Slide 4: General questions/comments to ACS
10. For all inserts there is a double level sensor (LT660+LT661, LT670+LT671, LT680+LT681).
  When the level is checked/is a condition in any of the sequences, only the first one is mentioned, i.e. LT660, although precisely that one is sitting on top of the other one, so how are the level probes considered in the control system? One writes LT660 but relates to both? or should one indicate exactly which one should be addressed? Example in Figure 1, with red markings).
  If it relates to both, then it would be best to address it in some other way (i.e. LT66total or LT vacuum or something else).
For the inserts, we use three different levels (LT660, LT670, LT680). We didn’t find probe enough length, also we will install two probes to measure for each liquid level. The control system will concatenate the two probe values, the user will see only one value.
11. Question: are all flow meters dry? In what follows, we have considered that all flow meters are oil-free and thus can be under vacuum.
I proposed the use of thermal flowmeters. There is no moving component inside these flowmeters (free oil). It is possible to use the thermal flowmeters in low pressure condition, but for our application, the pressure drop of these flowmeters is too high (higher than 0.5 mbar). The operating conditions of Gersemi flowmeters are defined for the pressure range close or higher than the atmospheric pressure (SHe at 3 bars).
Nota: In comparison with the Roots flowmeters, their measurement range is smaller than a factor 10.

## Slide 5: General questions/comments to ACS
12. We should all agree on a naming convention. In this document we have used magnet insert (instead of pressurized), liquid insert (instead of bath insert) and vacuum insert.
OK