## Slide 1
Carlos A. Martins
ESS – Accelerator Division – Power Converters section leader
LTH – IEA Department - Invited Adjunct Professor in Power Electronics
Klystron Modulators for ESS Accelerator
– Developments for Higher Efficiencies

## Slide 2
Powering scheme of one RF cell
- Example of Medium Beta and High Beta sections of the ESS Linac
Electrical pulsed power
Modulator
(Power Supply)
AC Electrical Network
RF cell #1
RF cell #N
Similar to RF cell #1
RF power
SC cavity #A
RF source A
RF power
SC cavity #B
RF source B
RF power
SC cavity #C
RF source C
RF power
SC cavity #D
RF source D
Beam
115 kV
100A
3.5 ms
14 Hz
3-phase, 600V AC, 50Hz
Approximately 33 RF cells in total (Medium Beta and High Beta)

## Slide 3
Pulsed Modulators for high power RF sources
– A machine challenging to design and procure
Sophisticated power electronic systems
modulator
1)- Multidisciplinary design:
Power Electronics; High Voltage; Mechanical;
Thermal and cooling;
Controls and software;
2)- Many different topologies possible;
Safety; Component’s availability;
Performance;
Availability / “Repairability”;
1m
Vertical klystron
modulator
3.8m
1.6m
High Voltage pulse quality
Pulse width
Rise time
Fall time
time
Flat-top
V
Reverse voltage
Heavy and bulky

## Slide 4
High cost impact in the whole accelerator
Few specialized companies worldwide, most of them SMB’s (Small Medium Business)
Engineering design capabilities;
Construction capacity and testing capabilities;
Quality Assurance and risk mitigation capacity;
AC electrical grid power quality
Current harmonic distortion & Power factor
Flicker (if pulsed with 10mHz<PRR<20Hz)
If conventional charging adopted, then ~15MW of pulsed power at 14Hz in the ESS power line
Flicker standard IEC 61000-3-2 and IEC 61000-3-11 (low voltage public grids)
14 Hz
(DV/V)max=0.3%
Pulsed Modulators for high power RF sources
– A machine challenging to design and procure

## Slide 5
Internal to the power converter structures:
  Power Semiconductors, Power inductors, Power transformers, Snubbers (if existent);
Pulse rise time:
  Energy sent to klystron during rise time is lost in the klystron collector due to RF driver inhibit until Vcathode stabilizes within 99..100% band;
Current harmonic distortion & power factor:
  AC power lines, AC grid transformers;
High efficiency means:
High performant power semiconductors (1.7kV technology) & moderate switching frequencies;
Advanced materials and design in power inductors and transformers;
Reduced rise times (controls, compromise in the filters design);
Low current harmonic distortion & unitary power factor & no flicker;
Pulsed Modulators Efficiency
– Where are the power losses?

## Slide 6
6
ESS has launched an Invitation To Tender for the design and construction of one 180kVA modulator (turn-key, functional specification):
  Contract awarded in Dec. 2011; Delivery May 2014 (30 months delivery time);
Strategies for developing modulators for ESS
– 1st strategy:
July
2011
1st ESS modulator (monolithic topology, pulse transformer based):
Rated 115kV/25A; 2.8ms/20Hz; 160kVA -> enough to power one 1.4MWpk klystron;
One section of the RF Gallery (8x 704 MHz RF sources)
Purple: AC line current
Green: Capacitor bank voltage
Limited performance:
Rise time = 350µs;
Flat-top droop = 3%;
Efficiency = 88%;
Power density = 22kVA/m2 (no space in RF Gallery)
AC power quality issues (flicker, current harmonic distortion)
High capital cost:
- ~130 modulators needed
8 modulators per RF cell needed

## Slide 7
Strategies for developing modulators for ESS
– 2nd strategy:
ESS has launched an Invitation To Tender for the design and construction of one 330kVA modulator (turn-key, functional specification):
  Contract awarded in June 2014; Delivery June 2017 (36 months delivery time);
Jan.
2014
2st ESS modulator (modular topology, HF transformers based):
Rated 115kV/50A; 3.5ms/14Hz; 330kVA -> enough to power two 1.4MWpk klystrons;
Better but still limited performance:
Rise time = ~100µs;
Flat-top droop < 1%;
Efficiency = 89%;
Power density = 66kVA/m2
Better AC power quality: still high current distortion;
Reliability concerns due to huge number of components and limited design margins
Still high capital cost:
- ~65 modulators needed

## Slide 8
Strategies for developing modulators for ESS
– 3rd strategy:
ESS has decided to launch a collaboration with LTH / IEA Department, in view of designing and building a modulator prototype for ESS, following a novel topology:
June
2013
3rd ESS modulator (Stacked Multi-Level topology)
Aimed at final ratings: 115kV/100A; 3.5ms/14Hz; 660kVA -> enough to power four 1.4MWpk klystrons;
Reduced scale prototype (easily scalable) rated at: 115kV/20A; 3.5ms/14Hz; 130kVA

## Slide 9
Pulsed modulators for klystrons
- Topology based on High Frequency transformers – Stacked Multi-Level (SML)
Modular topology, scalable to higher power levels;
Compact and cost effective;
High efficiency (92%);
Good pulse quality (low ripple, low rise-time);
Excellent grid power quality due to AFE’s (low flicker, low current THD);
High reliability (MTBF ~ 70’000 hours)

## Slide 10
SML modulator development and validation strategy:- Initial Plan
Contract placed for HV stage design, production & testing (requested delivery time: 9 months);
June
2014
LV stage (Part I)
Design studies, schematics, mechanical layout, BOM list, developed by ESS/LTH;
Construction subcontracted to a local company;
Signal cabling, controls software & hardware, and inspection held at LTH/IEA;
LV stage (Part I)
HV stage (Part II)
HV stage (Part II)
Turn-key system (design, construction, testing) outsourced to a another specialised company;
Study and design of LV stage completed. Contract placed for outsourcing LV stage assembly and cabling
Feb.
2014
Delivery of LV stage to LTH Test Stand;
Sept.
2014

## Slide 11
11
Jun ’13
Sept ’13 – May ’14
Apr ’14
Aug ’14
May ’14
Jan ’15
Experimental results, low voltage stage
Construction and testing of HV stage (oil tank assembly)
From Feb’15 …
The SML modulator development roadmap
(LV stage)

## Slide 12
SML modulator, LV stage validation
- Experimental results
Pulse (1kV)
AC line voltage
AC line current
Unitary power factor;
Sinusoidal line current, constant amplitude -> No flicker
Capacitor bank voltage
Capacitor bank charging current
Charging current adapted as an inversed function of the voltage;
Constant power flow
Active Front End (AFE) concept, well studied and developed at LTH / IEA
Controls & Human Machine Interface (Labview)
Part I - Low voltage power converter stage
Initial experimental results of the LV stage on dummy loads
Jan.
2015

## Slide 13
Cryo compressors
Beam Instrumentation
Neutron Instruments
Modulators
Modulators
400V
400V
140 kV
10 kV
600V
Cryo compressors
Beam Instrumentation
Neutron Instruments
Modulators
Modulators
10 kV
400V
600V
400V
SVC
SVC
- SVC footprint (outdoors): 2 x (10m x 15m) = 300 m2
- SVC estimated cost : 2 x ~6 M€ = ~12 M€
AC grid power quality:
– A classical approach with external grid compensators
Not required thanks to SML topology
(AFE + cap. charger control)

## Slide 14
HV stage design report from manufacturer showed prohibitive mechanical layout
Jan.
2015
SML modulator development and validation strategy:- Initial Plan
ESS/LTH design footprint (130kVA prototype)
ESS/LTH design footprint (660kVA full scale modulators
ESS/LTH decided to take over the design, as built to print, of the HV stage.
Work has started immediately
Jan.
2015
Contract with manufacturer cancelled
July
2015

## Slide 15
Part I – LV stage
Part II – HV module #1 prototype in oil tank
Experimental results at full power: Pulsed at 20kV/20A, 3.5ms/14Hz
(Note: no output filter present; waveforms are as expected)
HV module prototype in assembly workshop at LTH
Magenta: HV output pulse; Yellow: LV input voltage; Green: LV input current
3.5ms pulse
zoom
Complete integrated test of HV module prototype
Jul.
2015
HV stage (oil tank assembly) design and testing

## Slide 16
Silica gel breather
Tank lid
Inspection lid
HV output connector
Water cooling serpentine
HV stage (oil tank assembly) design and testing
Design of HV stage completed
June
2015
HV rectifier box
HVHF transformer
Fiberglass insulation frame
HV module
ESS launched ITT for construction of HV stage on a “build to print” basis
July
2015
HV stage construction contract awarded to AQ Elautomatik
Oct.
2015

## Slide 17
HV stage (oil tank assembly) construction
HV stage construction starts
Jan.
2016
Production of HV stage complete
Feb.
2016

## Slide 18
HV oil tank assembly received at test stand - 4th March 2016
Preliminary testing of HV oil tank assembly at low voltage - 24th March 2016;
1st testing at High Voltage - 4th April 2016
90kV with droop comp. - 18th April 2016
3 & 4 Testing of complete system
SML modulator prototype fully integrated tests
90kV achieved with full system (LV stage + HV stage)
Apr.
2016

## Slide 19
→ Heat run test successfully performed at nominal (115kV, 20A, 3.5ms/14Hz) for 12 hours consecutively
1st oil surprise: Ester MIDEL 7131 not suitable for >90 kV
Apr.
2016
Change type of oil to mineral Shell Diala
June
2016
Nominal voltage and power successfully achieved for 12 hours of consecutive operation
July
2016
Long term soak testing at nominal over >120 hours successfully achieved
Jan.
2017
SML modulator prototype fully integrated tests

## Slide 20
Mechanical integration.
Further testing on a real load (klystron)
200 hours of successful operation with real load (704Mhz Toshiba klystron)
Dec.
2017

## Slide 21
SML modulator, Full Scale design (660kVA)
- Supply of 4x 1.4MWpk klystrons in parallel
Retractable HV oil tank for easier access
Integrated oil spill bin
All in one frame with permanently mounted wheels for easy transportation
Total footprint: 3.8m x 1.4m
(planned was 5.5m x 1.6m, i.e. 40% less);
Total weight: < 5.5 tons (without oil);
Total volume of oil: ~ 2000 litters;
1.4m
3.8m
2.4m
Compact
HV module
Design of full scale modulator nearly completed, ready for call for tender
Sept.
2016

## Slide 22
Expect. performance:
Rise time = ~120µs;
Flat-top droop < 1%;
Efficiency = 91%;
Power density = 124kVA/m2
Excellent AC power quality: Active Front End;
(flicker free, sinusoidal current, unitary power factor)
Much improved reliability; minimal number of components (most are standard)
Effective capital cost (Mβ+Hβ):
33 modulators (~30 M€)
Rated 115kV/100A; 3.5ms/14Hz; 660kVA -> enough to power four 1.4MWpk klystron in //;
2 modulators per RF cell
SML modulator, Full Scale design (660kVA)
- Supply of 4x 1.4MWpk klystrons in parallel

## Slide 23
Klystron modulators’ cost model vs
SML modulator real cost
660
Cost reduction due to SML concept
Example #6:
ESS/SML modulators
Example #5:
ESS/Ampegon modulator
Doubling the power,
with only ~20% increase in cost;

## Slide 24
SML full scale modulator
- Initial test results on dummy load
Experimental results at nominal condition.
Blue: Output pulse voltage (10V=115kV); Green: Transformer primary current of one HV module (2.5kA/div). Six HV modules are placed inside the tank.
SML Pulsed Klystron modulator rated 115kV/100A ; 3.5ms/14Hz.
The Low Voltage power electronics structure is hosted in the top section of the frame.
The oil tank and retention bin is placed in the bottom side of the frame for ease extraction to the side during maintenance and testing.

## Slide 25
SML modulator #1 delivery and installation at ESS TS3
Extensive test campaign of the 1st 660kVA SML klystron modulator (RFQ) in factory, from April to May 2019, led by ESS staff :
  FAT was held on 9th May, at full power;
  Delivery to ESS on 27th May;
  Installation in TS3 finished on 5th June;
  SAT campaign started on 11th June and will be continued over ~1 month in TS3, on a HV dummy load;
ESS, TS3
factory
factory