## Slide 1: IOT operation in the SPS Long term experience TWC 800 MHz

## Slide 2: Project analysis slide 2
CONTENTS
SYSTEM PRESENTATION
OPERATION STATISTICS
800 MHZ OPERATION SCENARIO
IOTs LIFE TIME DATA
TRANSMITTERS FAULTS
IOT STARTUP MANAGEMENT
PREVENTIVE MAINTENANCE
EFFICIENCY
OTHER IOT INSTALLATION AT CERN
CONCLUSION

## Slide 3
SYSTEM PRESENTATION
2 x 800 MHz TW Cavity
160 KW CW per Cavity
TH795
CERN Accelerator complex

## Slide 4
OPERATION STATISTICS
In average there was around 7 hours off operation per year.
The availability for beam in SPS was more than 99.9 %
Chart: Operation hours
| hours operation
2015 | 7056
2016 | 6384
2017 | 6504
2018 | 6412
Chart: Downtime hours
| hours beam off | hours IOT off
2015 | 9.5 | 10.9
2016 | 4.5 | 11.5
2017 | 7.75 | 9.7
2018 | 5 | 7.5
Main objective

## Slide 5
800 MHZ OPERATION
SCENARIO
IOT
IOT
IOT
IOT
att
att
att
ph
ph
ph
load
load
load
load
load
load
CAVITY
att
3 dB
3 dB
3 dB
3 dB
3 dB
3 dB
L.L.
drive
IOT
IOT
IOT
IOT
att
att
att
ph
ph
ph
load
load
load
load
load
load
CAVITY
att
3 dB
3 dB
3 dB
3 dB
3 dB
3 dB
L.L.
drive
4 IOT combined for 1 cavity
The beam operation allows to have 1 IOT offline per cavity
And also, depending the users, the system allows to have 1 cavity off !
CAVITY 1
CAVITY 2

## Slide 6
IOT
IOT
IOT
IOT
att
att
att
ph
ph
ph
load
load
load
load
load
load
CAVITY
att
3 dB
3 dB
3 dB
3 dB
3 dB
3 dB
L.L.
drive
IOT
IOT
IOT
IOT
att
att
att
ph
ph
ph
load
load
load
load
load
load
CAVITY
att
3 dB
3 dB
3 dB
3 dB
3 dB
3 dB
L.L.
drive
4 IOT combined for 1 cavity
The beam operation allows to have 1 IOT offline per cavity
And also, depending the users, the system allows to have 1 cavity off !
800 MHZ OPERATION
SCENARIO
CAVITY 1
CAVITY 2

## Slide 7
IOT
IOT
IOT
IOT
att
att
att
ph
ph
ph
load
load
load
load
load
load
CAVITY
att
3 dB
3 dB
3 dB
3 dB
3 dB
3 dB
L.L.
drive
IOT
IOT
IOT
IOT
att
att
att
ph
ph
ph
load
load
load
load
load
load
CAVITY
att
3 dB
3 dB
3 dB
3 dB
3 dB
3 dB
L.L.
drive
4 IOT combined for 1 cavity
The beam operation allows to have 1 IOT offline per cavity
And also, depending the users, the system allows to have 1 cavity off !
800 MHZ OPERATION
SCENARIO
CAVITY 1
CAVITY 2

## Slide 8
CAVITY 2
IOT
IOT
IOT
IOT
att
att
att
ph
ph
ph
load
load
load
load
load
load
CAVITY
att
3 dB
3 dB
3 dB
3 dB
3 dB
3 dB
L.L.
drive
IOT
IOT
IOT
IOT
att
att
att
ph
ph
ph
load
load
load
load
load
load
CAVITY
att
3 dB
3 dB
3 dB
3 dB
3 dB
3 dB
L.L.
drive
4 IOT combined for 1 cavity
The beam operation allows to have 1 IOT offline per cavity
And also, depending the users, the system allows to have 1 cavity off !
800 MHZ OPERATION
SCENARIO
CAVITY 1

## Slide 9
LIFE TIME DATA
4 years of operation
6 tubes have now more than 30’000 hours filament
Only one had to be replaced current of 2018 with a ‘possible’ arc failure (still to be confirmed, the tube could be ok)
Chart: Filament hours TH795
| 732179 | 725777 | 740687 | 746447 | 753228 | 738648 | 753229 | 755767 + 790272
Commissioning | 5612 | 4065 | 3951 | 5831 | 6016 | 5878 | 5909 | 5958
2015 | 8112 | 8123 | 8201 | 8023 | 8078 | 8097 | 8083 | 8103
2016 | 7540 | 7612 | 7614 | 7569 | 7588 | 7623 | 7635 | 7644
2017 | 5747 | 5745 | 5750 | 5748 | 5655 | 5748 | 5729 | 5740
2018 | 6376 | 6392 | 4384 | 6438 | 6438 | 6438 | 6428 | 5433

## Slide 10
FAULTS
Chart: Intervention time in hours
| isolation transformer | RF lines | trolley | LL | PLC | water | crowbar unit | ion pump PS | arc IOT | grid PS | focus PS | air
2015 | 6 | 0 | 0 | 0 | 1 | 2 | 0 | 0.33333 | 0.083333 | 0.33333 | 0 | 0.16667
2016 | 9 | 0 | 0 | 0.5 | 1.5 | 0 | 0 | 0.33333 | 0.18333 | 0 | 0 | 0
2017 | 1.3333 | 4 | 2 | 1.5 | 0 | 0 | 0.33333 | 0 | 0.066667 | 0 | 0 | 0
2018 | 0.5 | 2 | 2 | 1 | 0 | 0 | 0.33333 | 0 | 0.05 | 0 | 0.33333 | 0

## Slide 11
FAULTS
Isolation Transformer :
  Resin transformer isolated up to 60 kV DC
  All first transformers installed come from a bad series
  During the two first years of operation, it was difficult to identify that the problem was the transformer
  New transformers were bought with an improved isolation
  Interventions were always necessary to fix the trouble, main circuit breaker tripped
Not a thermal cause !
But a HV arc!

## Slide 12
FAULTS
Coaxial lines :
  Some difficulties on the assemblies of the coaxial lines were experimented
  It was only human errors
  Can appear several days after the mistake was made.
  The time of intervention for repair is several hours
4-1/2’’ coaxial line
Bad contact from the inner clamp
Inner elbow burned

## Slide 13
FAULTS
Trolleys :
  The pieces between Ion pump et cathode melted due to a bad soldering.
  A second default was found, a water leak on the anode contact due to also a bad brazing
  The time to replace a trolley from the transmitter is as well several hours
Ion pump isolation piece
Anode cooling pipes

## Slide 14
FAULTS
Low Level and PLC :
  Following the LL upgrade done two years ago, the new ‘Switch & Limit’ system generated strange injections to the power system.
  Concerning the PLC and controls, we fixed some initial problems linked with the start-up, and later troubles linked with the ‘S&L” system.
‘Switch & Limit’ system generated harmonics (- 25 MHz / + 25 MHz) even higher than the fundamental !
800.8 MHz
776 MHz
825 MHz
Δ

## Slide 15
IOT STARTING UP
MANAGEMENT
Short stop (minutes)
IonPump & Filament : 10 min
HV (35 kV / 0.15 A) : 0 min
Long stop (hours or days)
IonPump & Filament : 2 hours
First start (at reception of the tube before storage or after a long (years) storage)
IonPump & Filament : 24 hours
RF (CW full power) : 0 min
Second start (after storage, less than a year)
HV ( 20 kV / 0.2 A) : 30 min
RF (CW half power) : 30 min
RF (CW full power) : 30 min
HV ( 30 kV / 0.2 A) : 30 min
HV ( 35 kV / 0.6 A) : 30 min
HV ( 35 kV / 0.15 A) : 30 min
HV ( 20 kV / 0.2 A) : 1 hour
HV ( 30 kV / 0.2 A) : 1 hour
HV ( 35 kV / 0.6 A) : 1 hour
HV ( 35 kV / 0.15 A) : 1 hour
RF (CW half power) : 30 min
RF (CW full power) : 30 min
IonPump & Filament : 2 hours
HV ( 20 kV / 0.2 A) : 30 min
HV ( 30 kV / 0.2 A) : 30 min
HV ( 35 kV / 0.6 A) : 30 min
HV ( 35 kV / 0.15 A) : 30 min
RF (CW half power) : 30 min
RF (CW full power) : 30 min
In case of more difficulties for the start up of an IOT, we do a conditioning on table up to 45 kV (35 kV in operation).
In addition we also reduce the filament current with respect to ageing given Thales indications.

## Slide 16
PREVENTIVE MAINTENANCE
Daily
Noise
Monthly
Air filter
Water inspection
Technical stop (4x1w/y)
Air pressure switch
IOT tunning
End year stop (10 w)
Long shutdown (1-2y/5y)
Electrical tightening
Smell
Reflected levels
Body current
Grid current
HV visual control
Combining IOT tunning
Tank water level
Soldering control
Smoke detector
Water flow
HV cleaning
Crowbar test
Drivers gain
Plunger control
Fans replacement
HV cleanig
Trolley cleaning
Motor servicing
Capacitors exchange
A good preventive maintenance get rid of troubles linked to HV

## Slide 17
PREVENTIVE MAINTENANCE
97 capacitors on 1 card
1,552 capacitors at 8 €/unit for 8 transmitters every 5 years !
Total cost = 2’500 €/year
Smoothing capacitors :
  The Low Voltage capacitors (400 VAC) for the HV smoothing in Electrosys cubicle is an important point for the maintenance and operation
  The lifetime in operation is rated 20’000 hours
  Off the shelf lifetime is 500 hours only !!!
  This implies a daily accurate management of the spares

## Slide 18
PREVENTIVE MAINTENANCE
Grid cleaning process :
  Following the recommendation from Thales, we do a grid cleaning
  The initial excess of barium from the cathode moves to the grid, and after around 5’000 hours this starts to induce thermal grid current
  We implemented our own system, and after our process the complete thermal grid current disappears by removing this excess of barium from the grid
  The cleaning was for the moment necessary only one time for each IOT

## Slide 19
EFFICIENCY
Chart: Pout vs Pin
| -10 | -6.9897000433601875 | -5.2287874528033758 | -3.9794000867203758 | -3.0102999566398121 | -2.2184874961635641 | -1.5490195998574319 | -0.96910013008056395 | -0.45757490560675118 | 0 | 0.41392685158225079 | 0.7918124604762482
Pout (KW) | 0 | 5 | 13.5 | 25.5 | 41.7 | 59.8 | 79.3 | 100 | 122 | 145 | 165 | 182 | 199
In order to guaranty availability for the beams, and include margin requested by the LLRF, we decided to operate the tubes at a lower point of operation than the maximum available.
We demonstrated that this is very efficient for the availability of the system.
However, this has a cost in the DC to RF efficiency, we pay almost – 15 % efficiency.
Chart: Pout vs Pin (4x IOTs)
| -10 | -6.9897000433601875 | -5.2287874528033758 | -3.9794000867203758 | -3.0102999566398121 | -2.2184874961635641 | -1.5490195998574319 | -0.96910013008056395 | -0.45757490560675118 | 0 | 0.41392685158225079 | 0.7918124604762482
Pout (KW) | 0 | 5 | 13.5 | 25.5 | 41.7 | 59.8 | 79.3 | 100 | 122 | 145 | 165 | 182 | 199
160 KW CW operation point
40 KW CW operation point

## Slide 20
SPS Crab cavity
400 MHz
40 KW CW
Medical RFQ
750 MHz
100 KW Pulsed
OTHER IOT INSTALLATION
@CERN
MB IOT
704 MHz
1.2 MW Pulsed

## Slide 21
Our IOT system is now mature and has proven to be very reliable, ensuring a high availability for the beams
IOT itself demonstrated to be very robust and easy to operate
IOT has the advantage of a high gain, needing only a few hundreds of Watt driver
IOT offers a high power density (HVPS can be aside and quite far away)
Given the LLRF requirements of margin, IOT offers a very good DC to RF efficiency
IOT are absolutely fantastic !
IOT should always be considered for RF systems for accelerators !
Thank you for your attention
CONCLUSION