## Slide 2
Nicolas GUILLOTIN (CERN)
on behalf of TE-CRG
SM18 CRYO UPGRADE
And major contribution of : F. DHALLA, J-P. LAMBOY, R. LAMY, , J. MOULEYRE, A. PERIN, M. PEZZETTI,
3rd International Workshop on Superconducting Magnet Test Stands
Uppsala - Sweden
2019, June 11 – 12
Ångström laboratory

## Slide 3
OUTLOOK
3
I | INTRODUCTION & CONTEXT
II | SM18 SIMPLIFIED CRYO DEVICES : BEFORE & AFTER UPGRADE
III | KEY FIGURES
V | OVERVIEW
2019 JUNE, 11
IV | UPGRADE HANDOVER & RESTART PROTOCOL

## Slide 4
SM18 : CERN main facility for testing SC accelerator magnets and SC RF cavities
SM18 cryo infrastructure is being significantly upgraded (starting in 2019) to meet requirements for :
LHC High Luminosity project (HL LHC)
R&D program for SC magnets
RF equipment until 2023 and beyond
RF cavities & Cryomodules
Horizontal test benches
2019 JUNE, 11
4

## Slide 5
Horizontal magnets test benches
Hor. Magn, feed box
Vertical magnet tests
Vertical magnet tests
RF cavities & CM tests
SC links tests
SOME OF THE SYSTEMS CURRENTLY IN OPERATION IN SM18
In Operation
5 vertical magnet cryostats :
HFM, CLUSTER D, SIEGTAL,
LONG, DIODES
10 Horizontal test benches for magnets
1 test bench for SC Link :
4 test benches for RF cavities : V3, V4, V5, V6
2 test benches for Cryomodules : M7, M9
1 independent test Bench :
Eu HIT GReC
2019 JUNE, 11
5
(80K, 4.5 K, 1.9 K)
(30 - 4.5 K, 2  15g/s)
(80K, 4.5 K, 1.9 K)
(4.5 K, 1.9 K)
(80K, 4.5 K, 1.9 K)
(10 - 4.5K)

## Slide 6
6kW Linde Cold Box
27g/s (700L/h) @4.5K
Purification units
Cool down - warm up unit (CWU)
Very Low Pressure compressors (WPU)
SOME DEVICE OF THE CRYOGENIC INFRASTRUCTURE CURRENTLY IN OPERATION
In Operation
2019 JUNE, 11
6
  Values per WPU unit :
  6 g/s @ 10 mbar
  12 g/s @ 20 mbar
  18 g/s @ 30 mbar (max)
3 x 130 Nm3/h Burckardt recovery compressors +
2 Purifiers 200 Nm3/h at 180 bars
2 x CWU 80g/s –
2 x 120kW @80K
With 3 Kaesers compressors

## Slide 7
New SC devices for the HL-LHC project require the SM18 cryostructure upgrade
FACING THE HL LHC PROGRAM
‘’HL-LHC IT STRING TEST’’, M. Bajko,
LHC Performance Workshop 2018 Chamonix
HL LHC String will be a new test stand to validate the collective behaviour of a structure including IT magnets
Low-β magnets - Nb3Sn technology - peak field of 11.4 T
With : 2 outer quadrupoles, Q1 & Q3 +
a central one divided into 2 identical magnets, Q2a and Q2b
Installation
Partial installation
11T dipoles
Standalone magnets
SC link
(Cables & current leads)
Crab RF cavities
Inner Triplet magnets
Project
Project

## Slide 8
8
I | INTRODUCTION & CONTEXT
II | SM18 SIMPLIFIED CRYO DEVICES : BEFORE & AFTER UPGRADE
III | KEY FIGURES
V | OVERVIEW
2019 JUNE, 11
IV | UPGRADE HANDOVER & RESTART PROTOCOL

## Slide 9
Magnet test benches: 2 vertical & 2 horiz. magnets at cold / month with 2 magnets powered simultaneously
Superconducting cavities: 1 cavity /2 weeks & 1 cryomodule test every 6 months
Parallel test of a superconducting link (SC Link) and/or the IT string (String)
Possibility of additional individual systems tests on dedicated facilities
REQUIREMENTS FOR THE UPGRADE OF THE CRYOGENICS INFRASTRUCTURE
BASED ON TEST PROGRAM - ASSUMPTIONS FOR COVERING THE MAIN TEST BENCHES

## Slide 10
SCHEMATIC LAYOUT OF THE SM18 CRYO INFRASTRUCTURE
Infra
Test benches
Cold Boxes
LHe dewar
GHe stock
Distribution
AFTER UPGRADE

## Slide 11
SM18 NEW COLD BOX
Mechanical Integration, Electrical and Control System review held at Linde Kryotechnik AG (LKT) in 2018 and beginning of 2019
Transport and arrival at the SM18
2019 MAY, 14
Cold Box installed in the SM18
2019 MAY, 15
2019 JUNE, 11
11

## Slide 12
SH18 NEW MAYEKAWA COMPRESSOR
Reception March, 26

## Slide 13
PROCESS UPGRADE FOR Nb3Sn MAGNETS
 Automated T control during cool down / warm up of Nb3Sn magnets has been implemented and need to be evaluated in real conditions
Installation of a new PT100 close to the magnet cold mass
Measurement of the T between CFB Temp_inlet – CFB Temp_outlet = value A
Measurement of the T between CFB Temp_inlet – Magnet new PT100 = value B
Continuous regulation of the T based on the max value : A or B
Redundancy for the PT100 is necessary
Particular case for the reconnexion after a trip
Nb3Sn SC magnet tests at the SM18 need a control of the T during cool down and warm up, in the 80 – 300K range

## Slide 14
Electrical cabinet installation for the 35g/s CB & Mayekawa CP
CP logic document sent to LKT, ready to be commissioned
CB logic sent to LKT
CONTROL & ELECTRIC UPGRADE
2019 : New rack with independent M580 PLC + RIO (Remote I/O)
2020 : M580 PLC moved to Infra Cabinet and RIO linked with fiber optic
PLC
RIO
Control & Elec upgrade for the SH18 :
SM18
SH18
Buffers and Burkhardt controlled by an independent system
Done
Done
2020
to allow independent maintenance and debugging
For the 35g/s Cold Box & Mayekawa compressor :

## Slide 15
15
I | INTRODUCTION & CONTEXT
II | SM18 SIMPLIFIED CRYO DEVICES : BEFORE & AFTER UPGRADE
III | KEY FIGURES
V | OVERVIEW
2019 JUNE, 11
IV | UPGRADE HANDOVER & RESTART PROTOCOL

## Slide 16
Sytem | Characteristics
EXISTING 6kW CB – ‘’LINDE A’’ | 27g/s (700L/h) @4.5K
NEW Linde CB – ‘’LINDE B’’ | 35g/s (1000L/h) @4.5K
Process compression station | 3 Stal He compressors (350 g/s @19 bar), 1.6 MW elec. power + ORS + new MAYEKAWA compressor (main drive motor of 1.4 MW)
Very Low Pressure Pumping (WPU) | 2 warm pumping units, each one : 6 g/s @ 10 mbar 12 g/s @ 20 mbar 18 g/s @ 30 mbar (max) To each WPU is dedicated a very low pressure heater of 32 kW (20g/s)
Pre-cooling to 80K | 2 x CWU (80g/s - 2 x 120kW @80K) - With 3 Kaesers compressors
GHe Purification | 5 x 80 m3 Balloons at 1 bar (3 Burckardt recovery compressors + 2 Purifiers 200 Nm3/h at 180 bars)
Pure GHe storage | 8 x 75m3 @18 bars
LHe storage | 1 x 25 m3 LHe storage at 1.6 bar (+ 1x 10 m3 mobile)
LN2 storage | 50’000L Dewar
SM18 CRYOPLANT GENERAL KEY FIGURES : AFTER UPGRADE
2019 JUNE, 11
16

## Slide 17
LHe CONSUMPTION FOR COOL DOWN TO 4.2K - COOL DOWN DURATION – STEADY STATE
The new 35g/s cold box will directly and significantly increase the LHe capacity for :
The cool down
The steady state
The Quench recovery
The 27g/s cold box will be dedicated to the HL LHC String and could complement the Dewar for the other test benches
Test benches
Test benches
2019 JUNE, 11
17
Cool down duration
Cool down consumption
Test benches
Steady state consumption
EQUIPMENT | LHe FLOW FOR QUENCH RECOVERY | QUENCH RECOVERY TIME
 | [g/s] | [h]
HFM | 12 | 4
Cluster D | 12 | 4
Horizontal dipoles | 14 | 2.25
LONG | 6.8 | 2

## Slide 18
SM18 TYPICAL CURRENT PLANNING : LHe DISTRIBUTION FOR THE TESTS
A priority management is currently essential for the cool down organisation (capacity limited to 27 g/s)
The 35g/s cold box will be mandatory to operate HL LHC String in parallel of the current tests and reduce Quench recovery time
2019 JUNE, 11
18

## Slide 19
19
I | INTRODUCTION & CONTEXT
II | SM18 SIMPLIFIED CRYO DEVICES : BEFORE & AFTER UPGRADE
III | UPGRADE KEY FIGURES
V | OVERVIEW
2019 JUNE, 11
IV | OPERATIONAL PROTOCOL & TOOLS AFTER THE UPGRADE

## Slide 20
RESTART PROTOCOL : CHECKLISTS
Could be implemented with CARPENTER
SAFETY
ORGANIZATION
COMMUNICATION
OPIMIZATION & TOOLS

## Slide 21
OPERATIONAL PROTOCOLS
Human safety  respect of rules and best practices for Operation
Equipment safety  preventive maintenance, follow up with INFOR
SAFETY
ORGANIZATION
COMMUNICATION
OPIMIZATION & TOOLS
‘’Weekly’’ general Coordination meetings for the tests (priority definitions)
Weekly Technical meetings
Reports on activities
Excel forecast tool to anticipate and simulate LHe consumptions

## Slide 22
SUMMARY
The upgrade of the cryogenic system at the SM18 gives the possibility to :
22
Increase the global LHe capacity for the Magnets and RF cavity tests
Allow the operation of the SM18 test benches while also running the test program of the HL-LHC String
Allow one CB/Compressor system to be under maintenance while the LHe supply to dewar can continue
 Operation flexibility & Redudancy in case of major issue
2019 JUNE, 11
Ease Quenches recovery for Magnet tests