## Front Page
FREIA Laboratory
Dept. of Physics and Astronomy
Uppsala University
Document No.: |  | Experiment Document No.: |  | Created: |  | 2013-06-21 | Page: | 1
|  |  |  | Modified: |  | 2019-08-21 | Rev. No.: | 3
Engineering Specification
ESS Spoke Cryomodule
Acceptance Testing
| Prepared by |  | Checked by |  |  |  | Approved by
FREIA team
Distribution List

## Changes
Revision | Date | History of Changes | Modifier
3.1 | 2019-08-21 | Update RF measurements items and order | HL,AM
Add oparate of gate vale
3 | 2017-11-22 | Add separate list of test items for prototype and series | HL
2.6 | 2017-11-21 | Add cool down of thermal shield | YS, RR
Add optimization of LLRF during cold conditioning
Add use of rest gas analyzer on cavity vacuum
2.5 | 2017-11-20 | Combine all tests with cold tuning system in one step | HL, RR
Remove LFD measurment step (was step 18)
Update cold measurement steps 14 through 19
2.4 | 2017-11-17 | Update required time for instrumentation, interlocks | RR
2.3 | 2017-11-15 | Update cold measurements | HL
Update the leak checking rate
2.2 | 2017-11-15 | Update cold measurements | RR
Cavity spectra: include Qext measurement
Set LLRF feedback test time to "0" = not foreseen
2.1 | 2017-11-07 | Update all entries based on comments FREIA team | RR
2 | 2017-11-02 | Add cavity vacuum check upon reception / inspection | RR
Move insulation vacuum connection after cryogenic lines
1.3 | 2016-12-07 | Update summary for 1 and 13 cryomodules | RR, RSK
|  | Add cold tuner verification at step 1e (initial inspection) | HL
|  | Add RF calibration at step 9d (instrumentation check in bunker) | HL
|  | Modify step 17, no Qe measurement, no pick-up measurement | HL
|  | Modify step 17, add 3-dB measurement, temperature effect | VG
1.2 | 2016-10-19 | Include the time for shipment | RR
1.1 | 2013-09-19 | Include the time required for arrival and unloading | RR
1 | 2013-09-17 | Overall update | RR
Draft | 2013-06-21 | Initial version | VG,RSK

## Procedure
ESS Spoke Cryomodule - Acceptance Testing at the FREIA Laboratory
Step | Process or Check Item | Overall Time [days] | In Bunker [days] | Team | Sub-step | Work Description | Acceptance Criteria | Check Sheet | Parts | Tools and Instruments | Utilities and Services
1 | Arrival, unloading | 0.5 |  |  | a | unloading |  |  |  |  | mobile crane, fork lift
[5 empty] | b | unpacking
[5 empty] | c | ship container back to sender
2 | Inspection | 2 |  |  | a | external inspection | no visual damage
[5 empty] | b | mechanical parts
[5 empty] | c | RF check | cavity spectrum, external Q |  |  | VNA
[5 empty] | d | cold tuner verification | piezo and stepper motor
[5 empty] | e | multipin thedthrough |  |  |  | multimeter, test box
[5 empty] | f | cavity vacuum | < 10-5 mbar
3 | Move into bunker | 0.5 | 0.5 |  |  | move the cryomodule into the bunker |  |  |  |  | overhead crane
4 | Cavity vacuum | 0 | 0 | VAC | a | connect lines and pumps | if cavity vacuum > 10-5 mbar |  |  | rest gas analyzer
[5 empty] | b | pump vacuum | <10 -5 mbar (<10-3 mbar for leak detection)
[5 empty] | c | leak detection | < 10-10 mbar l/s |  |  | helium leak detector
[5 empty] | d | open valve to cavity vacuum
5 | Cryogenic lines | 2 | 2 | CRYO | a | connect lines
[5 empty] | b | purging
[5 empty] | c | leak detection | < 10-8 mbar l/s |  | in parallel with step 5 | helium leak detector
6 | Instrumentation | 0 | 0 | CTRL | a | connect cables
[5 empty] | b | instrumentation check |  |  |  | multimeter, test box
[5 empty] | c | calibration ADCs etc |  |  |  | oscilloscope
[5 empty] | d | calibration RF loop | done at 353MHz |  |  | VNA, power meter
7 | Interlocks | 0 | 0 | CTRL |  | test interlocks |  |  | in parallel with step 5
8 | RF lines | 2 | 2 | RF | a | install doorknobs
[5 empty] | b | connect waveguides
9 | Insulation vacuum | 0.5 | 0.5 | VAC | a | connect lines and pumps | in parallel with step 8
[5 empty] | b | pump vacuum | < 10-5 mbar
[5 empty] | c | leak detection | < 10-8 mbar l/s
10 | Bunker doors |  |  |  |  | close main bunker gate
11 | Warm conditioning coupler | 6 | 6 | RF | a | detune RF source frequency
[5 empty] | b | conditioning coupler | reach full power, pulse length |  |  |  | RF source
12 | Cool down | 2 | 2 | CRYO | a | measure cavity frequency as function of temperature | continue during cool down |  |  | VNA
[5 empty] | b | cool down of the thermal shield
[5 empty] | c | close angle valve | around 200 K
[5 empty] | d | cool down to 4 K | in parallel with (b) |  |  |  | Liquefier, LN2
[5 empty] | e | measure cavity frequency sensitivity as function of pressure | during cool down 4 to 2 K
[5 empty] | f | cool down to 2 K |  |  |  |  | 2K pumps
[5 empty] | g | cooling coupler |  |  |  |  | SHe pumps
13 | Cold conditioning coupler | 1 | 1 |  |  | conditioning coupler | reach full power, pulse length
14 | Cavity spectra | 0.5 | 0.5 | RF | a | fundamental and HOM spectra |  |  |  | VNA
[5 empty] | b | Qpick-up
[5 empty] | c | Qload (3dB bandwidth)
15 | Cavity cold tuning system | 0.5 | 0.5 | RF, CTRL | a | test slow cavity tuners (stepper motor)
[5 empty] | b | measure tuning range and sensitivity (stepper motor)
[5 empty] | c | test fast cavity tuners (piezo)
15 | RF Calibration | 0.5 | 0.5 | RF, CTRL |  | CM cables re-calibration | done at 352.21MHz
16 | Cold conditioning coupler + cavity | 2 | 2 | RF | a | tune cavities on resonance |  |  |  | RF source, LLRF
17 | Measurements | 2 | 2 | CRYO, RF | a | Q0 by dynamic heat load | average over both cavities |  |  | RF source, LLRF
| Q0, Heat Load, Gradient |  |  |  | b | Eacc measurement (cross-check with Pt and Pf method )
| Filling time |  |  |  | c | X-ray emission | in parallel
| Multipacting |  |  |  | e | Onset and level of multipacting | in parallel
| Field emission |  |  |  | f | Onset and level of field emission | in parallel
18 | Long-term stability | 0 | 0 | CRYO, RF |  | long term stability test with PID + piezo | 4 hours at nominal operation with two cavities |  | in parallel with step 17
19 | Warm-up | 4 | 4 | CRYO | a | warm-up of cryomodule
[5 empty] | b | open angle valve | vacuum > 10-6 mbar
[5 empty] | b | open the main bunker gate
20 | Insulation vacuum | 0 | 0 | VAC | a | disconnect lines and pumps | in parallel with warm-up
[5 empty] | b | break vacuum with GN2 | T > 200 K ???
21 | RF lines | 2 | 2 | RF | a | disconnect RF waveguides
[5 empty] | b | de-install doorknobs
22 | Cryogenic lines | 0.5 | 0.5 | CRYO |  | disconnect cryogenics lines
23 | Instrumentation | 0 | 0 |  |  | disconnect instrumentation
24 | Move out of bunker | 0.5 | 0.5 |  |  | Move cryomodule outside bunker
25 | Inspection | 0.5
26 | Prepare for transport | 1
27 | Sub-total | 30.5 | 26.5
28 | Spare and wasted time | 6.1 | 5.3 |  |  | 20% according DESY statistics
29 | TOTAL | 36.6 | 31.8
| 1 cryomodules (excl. wasted time) | 30.5 | 26.5 | days
|  | 6.1 | 5.3 | work weeks
|  | 1.4524 | 1.2619 | months |  | national holidays and vacation time not taken into account
| 1 cryomodule (incl. wasted time) | 36.6 | 31.8 | days
|  | 7.32 | 6.36 | work weeks
|  | 1.7429 | 1.5143 | months |  | national holidays and vacation time not taken into account
| For 13 cryomodules | 475.8 | 413.4 | days
|  | 95.16 | 82.68 | work weeks
|  | 22.6571 | 19.6857 | months |  | national holidays and vacation time not taken into account

## Test item
ESS Spoke Cryomodule - Testing Items at the FREIA Laboratory
Step | Process or Check Item | Condition | Team | Sub-step | Work Description | Prototype test item | Series test item
1 | cavity spectrum and HOM | warm | RF |  | Get central cavity frequency and HOM spectrum | √ | √
2 | external Q | warm | RF |  | Simply estimate the coupling factor and Qe | √ | √
3 | coupler warm conditioning | warm | RF | a | reach full power, pulse length | √ | √
|  |  |  | b | get an optimal procedure for RF conditioning | √
4 | frequency shift vs. T | cool down | RF |  | Frequency shift due to cool down | √ | √
5 | static heat loads at 4 K | cool down | CRYO | a | without level regulation | √
|  |  | CRYO | b | with level regulation | √
6 | cavity level profile | cool down | CRYO |  | let the LHe evaporate to low levels (below 30%) | √
7 | frequency shift vs. Pressure | cool down | RF |  | Frequency shift due to pressure change from 4 to 2 K | √ | √
8 | static heat loads at 2 K | cold | CRYO | a | without level regulation | √
|  |  |  | b | with level regulation | √
|  |  |  | c | Effect of CV105 in heat load | √
|  |  |  | d | Cavity's power limit: apply heat power until the level and/or the pressure in the cavity shows instabilities | √
|  |  |  | e | Effect of different FPC cooling temperatures in heat load | √
9 | max. 2K pumps capacity at 2K | cold | CRYO |  |  | √
10 | coupler cold conditioning | cold | RF |  | reach full power, pulse length | √
11 | cavity package cold conditioning | cold | RF |  | reach nominal gradient ,full pulse length | √ | √
12 | central frequency and HOM | cold | RF |  |  | √ | √
13 | loaded Q and Qe | cold | RF | a | Get central cavity frequency and HOM spectrum at cold | √ | √
|  |  |  | b | Loaded Q ( -3dB bandwidth and decay time) | √ | √
|  |  |  | c | Qe | √
14 | measurements | cold | RF | a | Q0 by dynamic heat load | √ | √
| Q0, Heat Load, Nominal gradient |  |  | b | Eacc measurement (cross-check with Pt and Pf method ) | √ | √
| filling time |  |  | c | X-ray emission | √ | √
| multipacting |  |  | d | electron activity in coupler | √ | √
| field emission |  |  | e | Onset and level of multipacting | √ | √
| max gradient |  |  | f | Onset and level of field emission | √ | √
|  |  |  | g | Max gradient (Quench) | √
15 | dynamic Lorentz force detuning | cold | RF | a | Use oscilloscope (build in I/Q )to monitor the instantaneous frequency during pulse | √
|  |  |  | b | Use FPGA to check the frequency shit during the pulse | √ | √
16 | cavity cold tuning system | cold | CRTL,RF | a | test slow cavity tuners (stepper motor) | √ | √
|  |  |  | b | measure tuning range and sensitivity (stepper motor) | √ | √
|  |  |  | c | test fast cavity tuners (piezo) | √ | √
|  |  |  | d | excitation of mechanical modes | √
17 | stabilization of the cavity field with LLRF using only RF compensation | cold | CRTL,RF |  | stabilization of the cavity field only with LLRF power compensation | √
18 | long-term stability | cold | CRTL,RF |  | Stabilization of the cavity field with LLRF using both RF and piezo tuner compensation | √ | √
19 | frequency shift vs. Pressure | warm up | RF |  | Frequency shift from2 to 4 K | √
20 | frequency shift vs. T | warm up | RF |  | Frequency shift due to warm up | √